RESOLUTION NO. 2015-045

A RESOLUTION OF THE CITY COMMISSION OF THE CITY OF DANIA BEACH, FLORIDA, APPROVING THE SITE PLAN (SP-104-14) SUBMITTED BY CRAVEN THOMPSON AND ASSOCIATES, INC., ON BEHALF OF SDS DEVELOPMENT AND TRUST, LLC, C/O SHARON SHARABY, FOR PROPERTY LOCATED AT 2616-2648 GRIFFIN ROAD IN THE CITY OF DANIA BEACH, FLORIDA; PROVIDING FOR CONFLICTS; FURTHER, PROVIDING FOR AN EFFECTIVE DATE.

WHEREAS, Chapter 28, Part 6 of the Dania Beach Land Development Code (the “LDC”), Article 635, entitled “Development Review Procedures and Requirements”, states that site plan approval is required as a condition to the issuance of a building permit; and

WHEREAS, Craven Thompson and Associates, Inc., on behalf of SDS Development and Trust, LLC, c/o Sharon Sharaby (the “Applicant”) is requesting site plan approval to allow the construction of three (3) retail/office/commercial buildings with approximately 13,424 square feet to be located at 2616-2648 Griffin Road in the City of Dania Beach; and

WHEREAS, the City Commission conducted a duly noticed public hearing in accordance with Article 610 of the LDC;

NOW, THEREFORE, BE IT RESOLVED BY THE CITY COMMISSION OF THE CITY OF DANIA BEACH, FLORIDA:

Section 1.	That the site plan application (SP-104-14) and pervious area waiver are approved consistent with the site plan provided on record with the following conditions:

- Provide eight (8) foot wall or fence along the south property line (Planning).

- Provide channelized exit on SW 26th Avenue restricting south bound traffic into the residential neighborhood (Planning).

- Please specify if the underground utilities are existing or proposed; if proposed, provide documentation supporting the request to FPL and a date or time when this would occur (Landscape Consultant).

- Per LDC Section 275-100, other interior vehicular landscape areas shall be a minimum of 5 feet wide and 100 square feet in area, and there shall be no less than one tree for each two hundred square feet.  Please specify the area in square feet of the area where the monument sign is proposed to be installed (Landscape Consultant).

- Please provide percentage of other non-vehicular open space, and follow the requirements of LDC Section 275-140 (Landscape Consultant).

- Provide a pavement marking plan demonstrating all the following:

- All turning radii (demonstrated)

- Fire lane locations and striping detail (demonstrated)

- Drive aisle widths (demonstrated) and vertical clearances (noted)

- Fire Department Apparatus Access Road location and dimensions – demonstrate or note on the plan how they will be marked and delineated on site.

- Fire department access routes during construction – provide at permit application (BSO Fire).

- Provide a detail sheet accompanying the civil plans with the following details:

  - Fire hydrant detail;

  - Bollard/impact protection detail for hydrants, FDC’s and DDCV’s; and

  - Roadway pavement marker (RPM) detail for fire hydrant locations (blue reflective markers) (BSO Fire).

- Provide Fire flow demand calculations signed and sealed by licensed engineer (BSO Fire).

- Provide a statement of verification from the design professional of record, on official company letterhead, that the proposed water main sizing, fire hydrant spacing, and fire hydrant locations, are in compliance with the Broward County Land Use Code and the Florida Fire Prevention Code (This document shall bear the seal and signature of the engineer) (BSO Fire).

- Please correct the following deficiencies on your plan:

- Provide an additional fire hydrant to the NE corner of Griffin Road (one fire hydrant required every 300’);

- The fire hydrant water main must be a looped system; and

- Provide a scaled site plan (BSO Fire).

Section 2.	That such application must be reviewed by the Broward County Aviation Department.  The point of contact is William Castillo, Airport Planner located at 220 S.W. 45 Street, Suite 101, Dania Beach, Florida, 33312, (954) 359-6100.

Section 3.	That Pursuant to Section 635.100 “Expiration of Site Plans” of the Land Development Code, the Site Plan (SP-104-14), approval shall automatically expire and become null and void unless the Applicant files a complete building permit application with construction drawings for the improvements shown on the Site Plan, within eighteen (18) months from the date of this Resolution.

Section 4.	That issuance of a development permit by a municipality does not in any way create any right on the part of an applicant to obtain a permit from a state or federal agency, and does not create any liability on the part of the municipality for issuance of the permit if the applicant fails to obtain requisite approvals or fulfill the obligations imposed by a state or federal agency or undertakes actions that result in a violation of state or federal law.

Section 5.	That all resolutions or parts of resolutions in conflict with this Resolution are repealed to the extent of such conflict.

Section 6.	That this Resolution shall be in force and take effect immediately upon its passage and adoption.

PASSED AND ADOPTED on May 12, 2015.

ATTEST:

LOUISE STILSON, CMC					MARCO A. SALVINO, SR.

# CITY CLERK							MAYOR

# APPROVED AS TO FORM AND CORRECTNESS:

# THOMAS J. ANSBRO

CITY ATTORNEY